Gaseous Oxygen气态氧

General概述

Oxygen is the second largest component of the atmosphere, comprising 20.8% by volume. Gaseous oxygen is colorless, odorless, tasteless, and nonflammable. Oxygen is necessary to support life. It is a strong oxidizer that combines readily with many elements to form an oxide and is necessary to support combustion.

氧是空气的第二大组成成分，体积占20.8%。气态氧无色，无嗅，无味，不可燃。氧是维持生命的必要元素。氧是一种强氧化剂，很容易同许多元素反应，生成氧化物。氧还是维持燃烧的必需品。

Oxygen will react with nearly all organic materials and metals. Materials that burn easily in air will burn more vigorously in oxygen. Equipment used in oxygen service must meet stringent cleaning requirements; any system must be constructed of materials that have high ignition temperatures and which are nonreactive with oxygen under the service conditions. Vessels should be manufactured to American Society of Mechanical Engineers (ASME) codes and designed to withstand the temperatures and pressures involved.

氧几乎同所有的有机材料和金属发生反应。在空气中容易燃烧的材料在氧气中会燃烧的更加剧烈。氧气设施中使用的设备必须满足严格的清洁要求；系统必须采用具有高点火温度且在使用条件下同氧不反应的材料建造。容器的制造要满足美国机械工程师协会（ASME）的标准，容器的设计要使之能经受住有关的温度和压力。

Manufacture生产

Oxygen is produced by an air separation unit(ASU) through the liquefaction of atmospheric air and separation of the oxygen by continuous cryogenic distillation. The oxygen is then removed and stored as a cryogenic liquid. Oxygen can also be produced noncryogenically using selective adsorption processes to produce gaseous product.

氧的生产使用空气分离装置（ASU），通过大气的液化和连续低温蒸馏分离出氧。随后，氧以低温液体的状态搬运和储存。氧的生产还可以不采用低温的方法，而是采用选择性吸附过程来生产气体产物。

The ASU manufacturing process begins with a main air compressor and ends at the output of the product storage tanks. Air is compressed and sent through a clean-up system where moisture, carbon dioxide, and hydrocarbons are removed. The air then passes through heat exchangers where it is cooled to cryogenic temperature. Next, the air enters a high pressure distillation column where it is physically separated into a vaporous form of nitrogen at the top of the column and a liquid form of “crude” oxygen (~90% O2) at the bottom.

ASU生产过程从一个主气流压缩机开始，产品储存罐的输出后结束。空气通过一个去除了水蒸汽、二氧化碳和碳氢化合物的清洁系统压缩和输运。接着空气通过热交换器冷却到低温。随后空气进入高压分裂蒸馏塔，分离成氮蒸气和“原始”液氧（含大约90%的氧），氮蒸气在蒸馏塔顶部，液氧在蒸馏塔底部。

This crude oxygen liquid is withdrawn from the column and sent to a low-pressure column where it is distilled until it meets commercial specifications. The liquid oxygen is sent to a cryogenic storage tank.

接着从蒸馏塔取出原始液氧，送到一个低压塔，在这里继续蒸馏,直到满足商业技术规范。最后液氧送到低温储存罐储存。

Noncryogenic methods of air separation contain some of the same unit processes such as compression and clean-up, but differ in the fundamental technology to separate air into its components. Oxygen can be separated from nitrogen using Pressure/Vacuum Swing Adsorption (PSA/VSA) technology. Adsorption relies on a material (zeolite) that has the property of selectively adsorbing nitrogen while under a slight pressure and allowing oxygen to pass through. The adsorbed nitrogen is released from the zeolite by dropping the pressure to a lower level (often under vacuum)during the PSA/VSA process. When oxygen is produced by adsorption, argon flows through with the oxygen, producing oxygen with a purity range of 90-95%.

非低温空气分离方法使用一些同样的单元过程，如压缩和清洁，但在把空气分解成它的组成成分的基本技术上是不同的。使用压力/真空旋转吸附（PSA/VSA）技术可以把氧和氮分离开。吸附依赖于一种材料（沸石），该材料具有在微小的压力下选择性吸收氮而允许氧通过的性质。在PSA/VSA过程中，通过把压力降到更低的水平（通常在真空之下），可以把吸附的氮从沸石中释放出来。用吸附法生产氧时，让氩同氧一起流通，可以生产出纯度在90%到95%范围内的氧。

Uses用途

Oxygen is generally liquefied so it can be more effectively transported and stored in large volumes. However, most applications use oxygen in the gaseous form. The primary uses of oxygen relate to its strong oxidizing and life-sustaining properties. Oxygen is commonly relied upon in health and medical applications. Liquid oxygen is used as an oxidant for liquid fuels in the propellant systems of missiles and rockets..

通常要把氧液化，这样更便于大量运输和储存。但是，大多数应用使用气体形式的氧。氧的用途主要同它的强氧化性和维持生命的性质有关。在健康和医疗应用上，氧是必不可少的。在导弹和火箭的推进系统中氧用作液体燃料的氧化剂。

Oxygen is widely applied in the metal ndustries in conjunction with acetylene and other fuel gases for metal cutting, welding, scarfing, hardening, cleaning, and melting. Steel and iron manufacturers also extensively use oxygen or oxygen-enriched air to affect chemical refining and heating associated with carbon removal and other oxidation reactions. Benefits such as fuel and energy savings plus lower total emission volumes are realized when air is enriched or replaced with higher-purity oxygen.

同乙炔和其它燃料气体一起，氧广泛应用于金属工业的金属切割、焊接、嵌接、淬火、清洁和熔化。钢铁制造商还广泛使用氧或富氧空气来影响同除碳和其它氧化反应相联系的化学精炼和加热。使空气变成富氧空气或用高纯度氧替代空气有节约燃料和能量以及更小的总发射体积等好处。

In the chemical and petroleum industries, oxygen is used as a feed component to react with hydrocarbon building blocks to produce chemicals such as alcohols and aldehydes that contain oxygen in their structure. In many processes, the oxygen for reaction can be obtained from the use of air. However, direct use of oxygen, or enrichment of the air with oxygen, is necessary for some processes. There are several major petrochemical intermediates that are presently manufactured with high-purity oxygen including ethylene and propylene oxide (antifreeze), vinyl chloride(for PVC), and caprolactam (for nylon).

在化学和石油工业中，氧用作原料，同碳氢组分反应生产结构中含氧的化学品，如酒精和乙醛。在许多过程中，用于反应的氧可以从空气中获得。但是对于某些过程，直接使用氧或富氧空气是必要的。目前，几种重要的石化半成品是用高纯度氧生产的，包括乙烯、环氧丙烷（防冻剂）、氯乙烯（用于PVC）和己内酰胺（用于尼龙）。

The pulp and paper industry uses oxygen as a bleaching and oxidizing agent. A variety of process (liquor) streams show enhanced physical properties after treatment with oxygen; plant operating costs also improve.

纸浆和造纸工业使用氧作为漂白剂和氧化剂。用氧处理后，许多生产流程显示出增强的物理性质；工厂运转费用也降低了。

Similarly, oxygen enhances the combustion process in industries that manufacture glass, aluminum, copper, gold, lead, and cement or that are involved in waste incineration or remediation. There are corresponding productivity, energy, maintenance, and emissions benefits end-users may realize.

同样地，氧在许多工业中促进燃烧过程，这些工业包括玻璃、铝、铜、金、铅和水泥或者同垃圾焚化或回收相关的工业。终端用户可以在相应的生产率、能量、维护和散发污染物方面获得好处。

Wastewater treatment plants successfully employ oxygen to enhance their chemical process efficiency. Aquaculturists such as fish-farmers also see benefits in the health or size of their livestock when the host environment is oxygenated.

废水处理厂成功地利用氧提高了他们的化学过程的效率。当居住环境用氧处理后，水产养殖者，如渔民还会在他们的牲畜的健康或体形大小方面受益。

Health Effects对健康的影响

Normally air contains 21% oxygen and oxygen is essentially nontoxic. No health effects have been observed in people exposed to concentrations up to 50% at 1atmosphere for 24 hours or longer.

正常情况下空气中含21%的氧，而且氧是无毒的。在暴露于含氧高达50%、压力为1个大气压的空气中24小时或更长的人群中没有观察到对健康的影响。

The inhalation at 1 atmosphere of 80%oxygen for more than 12 hours can cause irritation of the respiratory tract, progressive decrease in vital capacity, coughing, nasal stuffiness, sore throat, and chest pain, followed by tracheobronchitis and later by pulmonary congestion/edema.

在含氧80%、压力为1个大气压的空气中呼吸超过12小时会导致刺激呼吸道，渐进性肺活量减少，咳嗽，鼻阻塞、疼痛/水肿。

Inhalation of pure oxygen at atmospheric pressure or less can cause pulmonary irritation and edema after 24 hours.

在大气压或更低气压下吸入纯氧，24小时后会导致肺刺激和水肿。

Respiratory symptoms can occur in two to six hours at pressures above 1 atmosphere. One of the earliest responses of the lung is accumulation of water in the interstitial spaces and within the pulmonary cells. This can cause reduced lung function, which is the earliest measurable sign of toxicity. Other symptoms include fever, and sinus and eye irritation.

当压力在1个大气压以上时，2到6个小时内会出现呼吸系统病症。肺的最早的反应之一是在空隙和肺细胞内的积水。这会导致肺功能减退，这是可以测量的最早的中毒迹象。其它症状包括发烧、瘘管和眼睛受到刺激。

When pure oxygen is inhaled at pressures greater than 2 or 3 atmospheres, a characteristic neurological syndrome can be observed. Signs and symptoms include nausea, dizziness, vomiting, tiredness, light-headedness, mood changes, euphoria, confusion, incoordination, muscular twitching, burning/tingling sensations particularly of the fingers and toes, and loss of consciousness. Characteristic epileptic-like convulsions, which may be preceded by visual disturbances, such as loss of peripheral vision, also occur. Continued exposure can cause severe convulsions that can lead to death. The effects are reversible after reduction of oxygen pressure.

当吸入压力大于2或3个大气压的纯氧时，可以观察到典型的神经系统症状。迹象和症状包括恶心、眩晕、呕吐、疲倦、烧灼/麻刺感（特别是手指和脚趾的）、失去知觉。还会发生典型的象癫痫一样的抽搐，之前还可能会发生视觉障碍，如丧失间接视力。连续暴露会引起可能导致死亡的抽搐。在降低氧的压力后影响是可逆的。

Premature infants placed in incubators to breathe oxygen in concentrations greater than in air can develop irreversible eye damage. Within six hours after an infant is placed in a high -oxygen atmosphere, vasoconstriction of the immature vessels of the retina occurs, which is reversible if the child is immediately returned to air but irreversible if oxygen-rich therapy is continued. Fully developed blood vessels are not sensitive to oxygen toxicity.

早产儿保育器中的早产婴儿呼吸浓度大于空气中浓度的氧会导致不可逆转的视力损害。婴儿置于含氧浓度高的空气中6个小时以内，未发育成熟的视网膜血管会发生血管收缩。如果立刻把孩子转移到空气中，这是可逆的，如果富氧治疗继续的话，会变成不可逆的。充分发育的血管对氧中毒是不敏感的。

Containers容器

Gaseous oxygen is shipped and stored in high-pressure cylinders, tubes, or tube trailers depending on the quantity required by the user. Cylinders are designed and manufactured according to applicable codes and specifications for the pressures and temperatures involved. Cylinders are manufactured according to Department of Transportation(DOT) regulations, which specify the material of construction, method of manufacture, testing, and what products they are permitted to be filled, as well as other details. The quantity of product a container can hold is determined by its pressure rating and internal volume. Generally the higher the pressure, the more oxygen is contained in a cylinder.

根据用户要求的量，使用高压钢瓶、管道或管道拖车来运输和储存气态氧。钢瓶的设计和制造是按照相应的压力和温度所适用的法规和规范。钢瓶的制造依照交通部的规定，该规定指定了建材、制造和测试方法、允许填充的产品以及其它细节。容器能够容纳的产品数量由它的额定压力和内容积决定。一般来说，压力约高，钢瓶内装的氧越多。

Table 1: Gaseous Oxygen Physical and Chemical Properties

表1：气态氧的物理和化学性质

Chemical Formula化学分子式  O2

Molecular Weight分子量  31.999

Boiling Point沸点 @ 1 atm  –297.4°F (–183.0°C)

Freezing Point凝固点 @ 1 atm  –361.9°F (–218.8°C)

Critical Temperature临界温度  –181.8°F (–118.4°C)

Critical Pressure临界压力  729.1 psia (49.6 atm)

Density密度, Liquid液体, @ BP, 1 atm  71.23 lb/scf

Density密度, Gas气体 @ 68°F (20°C), 1 atm  0.0831 lb/scf

Specific Gravity比重, Gas (air=1)气体（空气=1） @ 68°F (20°C), 1 atm  1.11

Specific Volume比容 @ 68°F (20°C), 1 atm  12.08 scf/lb

Latent Heat of Vaporization汽化潜伏热  2934 Btu/lb mole

Expansion Ratio, Liquid to Gas, 膨胀率，液体到气体BP to 68°F (20°C)  1 to 860

Solubility in Water水中的溶解度 @ 77°F (25°C), 1 atm  3.16% by volume.

Cylinders钢瓶

A cylinder is a hollow tube with a closed concave base that permits it to stand upright. The opposite end is tapered to a small opening that is threaded to accommodate the installation of a valve. A threaded neck ring is attached to the tapered end so that a protective cylinder cap can be installed. Cylinders may be used individually or in groups. When used in groups, the cylinders should be piped together, for either stationary storage or to form portable banks.

钢瓶是中空的管道，封闭的底部是凹入的，这样可以直立起来。另一端是锥形开口，车有螺纹，以便安装阀门。锥状顶端装有带螺纹的颈环，可以安装保护性的钢瓶帽。钢瓶可以单个或成群使用。成群使用时，钢瓶要用管道连接到一起作为固定储存库或形成移动储存库。

Tubes管道

A tube is a pipe tapered at both ends. Each end is threaded to allow the installation of valves, connections, or relief devices.

管道两端是锥形。每一端都车有螺纹，以安装阀门、接头或减压装置。

Tubes are manufactured according to DOT regulations or they may be made to ASME codes, depending upon whether they are used for transportation or mounted permanently at a site. Tubes are generally mounted on a truck-trailer chassis or railcar bed, or placed at stationary locations when large amounts of oxygen are needed.

根据管道是用于运输还是永久安装在某处，按照DOT的规定或者ASME的规定制造管道。管道一般是安装在拖车底盘或有轨车底座上，或者当需要大量氧时放置在固定位置。

Valve Connections阀门接头

The Compressed Gas Association (CGA) recommends three different connections for oxygen depending on the pressure of the container.

根据容器的压力，压缩气体协会（CGA）推荐了三种不同的接头。

In addition, a high-integrity connection also known as a Diameter Index Safety System(DISS) connection has been assigned to oxygen service; medical post-type valves are assigned a yoke connection. See Table 2 for details. For detailed drawings of these connections consult CGA Pamphlet V-1. For general drawings consult the Air Products “Specialty Gases and Equipment Catalog.”

另外，指定了一种被称为直径指数安全系统（DISS）的高完整性接头用于氧设施；医用柱状阀门被指定使用卡箍接头。详细情况见表2。要知道这些接头的详细图纸可以参考CGA手册V-1。要知道草图可以参考Air Products的“特种气体和装置目录”。

WARNING: NEVER use adapters to make cylinder connections!!!

警告：严禁使用转换接头进行钢瓶的连接！！！

Pressure-Relief Devices减压装置

Oxygen containers are equipped with pressure-relief devices to protect from over pressurization and possible rupture. Cylinders less than 65” long use a rupture disk device. Cylinders over 65” use a combination device consisting of a rupture disk backed by a fusible alloy. Combination devices require that both the temperature and pressure requirements be reached before the device will relieve. For more information on pressure-relief devices consult Air Products’ Safetygram-15, “Cylinder Pressure-Relief Devices.”

氧容器装备有减压装置，以便在过压和可能的破裂时保护容器。长度小于65英寸的钢瓶使用破裂盘装置。大于65英寸的钢瓶使用由后面是可熔合金的破裂盘组成的组合装置。组合装置要求在装置减压前温度和压力都达到要求。要了解关于减压装置的更多情况，可以参考Air Products的安全程序-15，“钢瓶减压装置”。

Container Stampings钢瓶的印记

Each cylinder or tube is identified by stampings in the metal of the shoulder. Fig. 3 depicts an example of these stampings and what they mean.

可以通过肩部金属上的印记来鉴别每一个钢瓶或管道。图3描述了一个印记的例子和它们的含义。

Shipment of Gaseous Oxygen气态氧的运输

All shipments of compressed oxygen must comply with DOT regulations. This applies to motor freight, rail, air, and water shipments. For air shipments, all packages must also comply with International Air Transport Association / International Civil Air Organization (IATA/ICAO) Dangerous Goods regulations. Water vessel shipments must also be prepared in accordance with the International Maritime Organization (IMO)regulations. All packaging used to transport oxygen must be either “UN/DOT Specification” or “UN/DOT Authorized” and in proper condition for transport. DOT Code of Federal Regulations, Title 49, also specifies the following labeling and identification requirements:

所有压缩氧的运输必须遵守DOT的规定。这对汽车货运、铁路、空运和水运都有效。对于空运，所有包装还要遵守国际空运协会/国际民航协会（IATA/ICAO）危险货物的规定。水运还要遵守国际海运组织（IMO）的规定。所有用于运输氧的包装必须或者是“UN/DOT规范”或者是“UN/DOT授权”，而且状态良好。DOT Code of Federal Regulations的第49条还规定了下列的对标签和鉴别的要求：

DOT Shipping Name货物名称: Oxygen, Compressed氧，压缩的

DOT Hazard Class危险等级: 2.2

DOT Shipping Label货物标签: Nonflammable Gas and Oxidizer (For domestic shipments only the oxygen label may be used)不可燃气体和氧化物（对于国内运输，只可以使用氧标签）

Identification Number鉴别号: UN1072

Fig. 1 Typical cylinder shapes and sizes.图1 典型的钢瓶形状和尺寸

1. Cylinder Specification钢瓶规范

• DOT–Department of Transportation, which is the regulatory body that governs the use of cylinders.

DOT-交通部，管理钢瓶使用的管理部门

• Specification of the cylinder type of material of construction (e.g., 3AA).钢瓶建材类型的规定（如3AA）

• Service or working pressure in pounds per square inch (e.g., 2,265 psi)设施或工作压力，单位为磅每平方英寸（如2,265 psi）

2. Cylinder Serial Number钢瓶序列号

• The letters SG precede the serial numbers for Specialty Gas cylinders.对于特种气体钢瓶，字母SG标在序列号之前

3. Registered Owner Symbol登记的所有者符号

• Symbol used to indicate the original owner of the cylinders.符号用于指示钢瓶的最初所有者。

• APROINC is a Registered Owner Symbol for Air Products. APROINC是Air Products的登记的所有者符号。

4. Date of Manufacture生产日期

• This date (month-year) also indicates the original hydrostatic test.该日期（月-年）还说明了最初的流体静力学测试的日期。

5. Neck Ring Identification颈环鉴别

• The cylinder neck ring displays the name of the current owner of the cylinder.颈环显示着钢瓶现在的所有者的名字。

6. Retest Markings再测试记号

• The format for a retest marking is: Month–Facility–Year–Plus Rating–Star Stamp.再测试记号的格式是：月-设备-年-过量等级-星形标记

• The + symbol (Plus Rating) indicates that the cylinder qualifies for 10% overfill.加号（过量等级）说明钢瓶可以过量灌装10%

• The H symbol (Star Stamp) indicates that the cylinder meets the requirements for 10-year retest.符号H（星形标记）说明钢瓶满足10年后再测试的要求

7. CylinderTrak钢瓶的追踪

Bar Code Label条形码标记

• The Cylinder Trak bar code label provides a unique cylinder identifier and is used by computer systems

to track cylinders throughout the fill process. As an optional service, we have the capability of tracking cylinders to and from customers.

钢瓶的条形码标记为每个钢瓶提供了唯一的标志符号，计算机系统用它来在整个灌装过程中追踪钢瓶。作为一项可以选择的服务，我们有追踪来往于消费者的钢瓶的能力。

8. Cylinder Manufacturer’s Inspection Marking钢瓶制造商的检测标记

9. Cylinder Tare (Empty) Weight钢瓶皮（空）重

Fig. 3 Key to cylinder stampings.钢瓶印记的说明

Table 2: Oxygen Service Connections表2：氧设施的接头

Cylinder Service钢瓶维护

CGA Connection  CGA接头

Oxygen氧 < 3000 psig x 540

Oxygen氧 at 3001 to 4000 psig  577

Oxygen氧 at 4001 to 5500 psig  701

Medical oxygen with post valve带有柱状接头的医用氧  870

Semiconductor半导体  714

Fig. 2 A typical tube container system for gaseous oxygen..图2 一个典型用于气态氧的管道容器系统

Safety Considerations对安全的考虑

Fire is the primary hazard associated with gaseous oxygen. Although nonflammable, oxygen readily supports combustion. Explosions may occur in locations where a mixture of fuel gas and oxygen can accumulate.

火是同气态氧相联系的主要危险。尽管氧本身不可燃，但它很容易支持燃烧。在燃料气体和氧能够积累起来的地方可能发生爆炸。

It is important to note that fire chemistry starts to change in oxygen-enriched environments. The CGA has established the definition of an oxygen-enriched atmosphere as being any atmosphere containing at least 23% oxygen. Materials easily ignited in air not only become more susceptible to ignition, but also burn with added violence. These materials include clothing and hair, which have air spaces that readily trap oxygen. Oxygen levels of 23% can be reached very quickly and all personnel must be aware of the hazard.

在富氧环境里起火的化学性质开始变化，注意到这一点是很重要的。CGA将至少含有23%的氧的大气定义为富氧大气。在空气中容易点燃的材料（在富氧大气中）不仅变得更容易点燃而且燃烧得更加剧烈。这些材料包括衣服和头发，它们内部的空间很容易储存氧。含氧量23%是可以非常迅速地达到的，所有人都必须意识到这种危险。

Systems used in oxygen service must meet stringent cleaning requirements to eliminate any incompatible contaminants. CGA Pamphlet G-4.1, “Cleaning Equipment for Oxygen Service,” describes cleaning methods for equipment used in oxygen service and CGA Pamphlet O2-DIR, “Directory of Cleaning Agents for Oxygen Service,” provides comparative information on cleaning agents used to clean oxygen equipment. Also, review the appropriate Material Safety Data Sheet (MSDS).

用于氧设施的系统必须满足严格的清洁要求，排除任何不相容的污染物。CGA手册的G-4.1，“氧设施的清洁装置”，描述了用于氧设施的装置的清洁方法。CGA手册的O2-DIR，“氧设施的清洁剂目录”，提供了有关用于清洁氧设备的清洁剂的有关信息。还可以回顾一下合适的材料安全数据表（MSDS）。

Buildings建筑物

Adequate ventilation must be provided in areas where oxygen is in use. Keep them clear of combustible materials and post signs indicating the hazard. Also post “No Smoking” signs. Test the atmospheres in confined work areas for oxygen content. Oxygen-enriched atmospheres can cause materials that burn in air to burn more violently or even explosively. Oxygen concentrations in excess of 23% increase the hazard exposure to personnel and material.

必须为正在使用氧的地方提供充分的通风。保持可燃材料的清洁，同时张贴说明危险的标记。还要张贴“禁止吸烟”的标记。测试狭窄工作空间内空气中氧的浓度。富氧空气会导致在空气中可燃的材料燃烧得更剧烈，或者甚至发生爆炸。氧浓度超过23%增加了暴露于其中的人员和材料的危险。

Remember, oxygen has no warning properties!

记住，氧没有警告性特征！

Storage储存

•Cylinders should be stored upright in a well-ventilated, dry, cool, and preferably fire-resistant, secure area, which is protected from the weather

钢瓶应该直立储存在通风良好、干燥、凉爽、最好防火的安全的不受天气影响的地方。

•Storage temperatures should NEVER exceed 125°F (52°C) and the area should be free of combustible materials. Storage should be away from heavily traveled areas and emergency exits.

储存室温度禁止超过125°F (52°C)，而且不能有可燃材料。储存地应远离人员经常出入的地方和紧急出口。

• Oxygen must be separated from flammables and combustibles by 20 feet or a half-hour fire wall.

氧必须同可燃物和易燃物间隔至少20英尺，或者间隔一道半小时的防火墙。

• Post “No Smoking” and “No Open Flames” signs. Copies of signs maybe downloaded from Air Products’ Product Stewardship web site at www.51qiti.com.

张贴“禁止吸烟”和“禁止明火”的标志。这些标记的拷贝可以从Air Products的网站上下载，网址是www.51qiti.com。

•Avoid areas where salt or other corrosive materials are present. Valve protection caps and valve outlet seals should remain on cylinders not connected for use.

避免储存在有盐或其它腐蚀性材料的地方。不使用时，阀门保护帽和阀门排气口密封应保持在钢瓶上。

•Separate full from empty cylinders. Avoid excessive inventory or storage time and keep good inventory records

把空钢瓶和满钢瓶隔离开。避免库存过多和储存时间过长，做好库存记录。

•Use a first-in first-out (FIFO) system.

采用先进先出（FIFO）库存管理系统

Fig. 4 Oxygen shipping label..图4氧的运输标签

Handling操作

•Use only oxygen compatible lubricants.

只使用同氧相容的润滑剂

•If you experience any difficulty operating the container valve or with the container connections, discontinue use and contact the supplier. Use the proper connections.

如果你在操作容器阀门或容器接头时遇到任何困难，马上停止使用，并同供应商取得联系。使用正确的接头。

•DO NOT USE ADAPTERS!禁止使用转换接头！

•Do not remove or interchange connections.禁止移动或交换接头

•Use piping and equipment designed to withstand pressures to be encountered.

使用设计得可以承受遇到的压力的管道和设备

•It is recommended that all vents be piped to the exterior of the building.

建议所有的通风孔都输送到建筑物外部。

•Use a suitable hand truck designed for cylinder movement. Do not drag, roll, or slide containers on their sides.

使用设计用于钢瓶搬运的合适的手推车。禁止拖拉、旋转或滑动容器。

•Never attempt to lift a cylinder by its cap.禁止试图提着钢瓶帽举起钢瓶。

•Secure cylinders at all times while in use.使用时要一直保持钢瓶固定。

•Use a pressure reducing regulator or separate control valve to safely discharge gas from cylinder.

使用减压调整器或单个的控制阀来安全地从钢瓶中排出气体。

•Use a check valve to prevent reverse flow into the cylinder.

采用止回阀，防止回流入钢瓶。

•Do not overheat cylinder to increase pressure or discharge rate.禁止使钢瓶过热来增加压力或流速。

•NEVER insert an object (e.g., wrench, screwdriver, pry bar, etc.) into valve cap openings. Doing so may damage the valve causing it to leak.

禁止把物体（如扳手、螺丝起子、撬杆等）插入阀门帽的开口处。这样做可能损伤阀门，导致泄漏。

•Use a special cap wrench or adjustable strap-wrench to remove over tightened or rusted caps.

使用专门的阀门帽扳手或活动扳手来卸开过紧或生锈的帽子。

Refilling or shipping compressed gas cylinders without the consent of the owner is a violation of Federal law.

未经所有者同意重新灌装或运输压缩气体钢瓶是侵犯联邦法律的行为。

Personal Protective Equipment (PPE)个人防护装备(PPE)

Personnel must be thoroughly familiar with properties and safety considerations before being allowed to handle oxygen and its associated equipment. Safety glasses, safety shoes, and leather work gloves are recommended when handling cylinders.

在被允许使用氧和它的附件之前，操作人员必须对它们的性质和安全问题十分熟悉。当操作钢瓶时，推荐使用安全眼镜、安全鞋和皮制工作手套。

Only trained and certified emergency responders should respond to emergency situations. In emergency situations, self-contained breathing apparatus (SCBA) must be used. Clothing which is fire-resistant in air may be readily ignitable in oxygen-enriched atmospheres.

只有训练有素的被认可的紧急反应人员才可以对紧急形势做出反应。紧急形势下，必须使用自给式呼吸器。在空气中防火的衣服在富氧大气中可能很容易着火。

First Aid急救

When breathing oxygen mixtures are used at pressures above 1 atmosphere, seek medical advice for proper health instructions.

当呼吸压力在一个大气压以上的氧混合物时，寻求医生的建议，以得到正确的健康指导。

Fighting Fires救火

Since oxygen is nonflammable, but supports combustion, fire-fighting actions require shutting off the source of oxygen, if possible, then fighting the fire according to the material involved. Most cylinders are designed to vent contents when exposed to elevated temperatures. However, upon exposure to intense heat or flame, a cylinder may vent rapidly and/or rupture violently.

既然氧本身不可燃但支持燃烧，救火行动要求尽可能切断氧源，然后按照燃烧的材料来救火。大多数钢瓶设计得可以在暴露于高温时排出内容物。但是，暴露于剧热或火焰时，钢瓶会迅速排出内容物和/或猛烈地破裂。

Emergency Response System紧急反应系统

• Call呼叫: +1 (800) 523-9374 (Continental U.S. and Puerto Rico美国大陆和波多黎各)

• Call呼叫: +1 (610) 481-7711 (Other locations其它地方)

• 24 hours a day, 7 days a week一天24小时，一周七天

• For assistance involving Air Products and Chemicals, Inc. gases and equipment.

Technical Information Center技术资料中心

• Call呼叫: +1 (800) 752-1597 (U.S美国.)

• Call呼叫: +1 (610) 481-8565 (Other locations其它地方)

• Fax传真: +1 (610) 481-8690

• E-mail电子邮件: gasinfo@apci.com

• Monday星期一–Friday星期五, 8:00 a.m.–5:00 p.m. EST

Product Safety Information产品安全资料

• For MSDS and Safety grams需要材料安全数据表和安全程序:

• Fax-on-Demand应要求发传真:

Call呼叫: 020－34507954

• Enter MSDS Index No. 1000 for a complete list of available safety literature.

进入材料安全数据表第1000号可以获得现有的安全文献的全部目录

• 24 hours a day, 7 days a week一天24小时，一周七天