Gaseous Argon气态氩

General概述

Gaseous argon is tasteless, colorless, odorless, non corrosive, and nonflammable. Argon belongs to the family of rare inert gases. It is the most plentiful of the rare gases making up approximately 1% of the earth’s atmosphere. It is monatomic and extremely inert, forming no known chemical compounds.

气态氩无味，无色，无嗅，无腐蚀性，不可燃。氩属于稀有惰性气体家族。它是最丰富的稀有气体，占地球空气的约1%。它是单原子，极不活泼，没有已知的化合物。

Special materials of construction are not required to prevent corrosion. Vessels and piping should be designed to American Society of Mechanical Engineers (ASME) or Department of Transportation (DOT) codes for the pressures and temperatures involved.

不要求特殊的建材来防止腐蚀。容器和管道系统要根据相关的压力和温度按照美国机械工程师协会（ASME）或交通部（DOT）的规定来设计。

Argon may be compressed into cylinders by water or oil-lubricated compressors or by dry compression systems. To determine the amount of argon in a cylinder, use the appropriate pressure and temperature capacity chart for a specific size cylinder. (The higher the pressure, the larger the amount of argon in the container.)

氩可以使用水或油润滑的压缩机或干压缩系统压缩进钢瓶。要确定钢瓶的氩容量，对于特定尺寸的钢瓶使用合适的压力和温度容量表。（压力越大，容器的氩容量越大）

Manufacture生产

Argon is produced by an air separation unit(ASU) through the liquefaction of atmospheric air and separation of the argon by continuous cryogenic distillation. The argon is then removed as a cryogenic liquid.

氩的生产使用空气分离装置（ASU），通过大气的液化和连续低温蒸馏分离出氩。随后，氩作为低温液体运输。

The ASU manufacturing process begins with a main air compressor and ends at the output of the product storage tanks. Air is compressed and sent through a clean-up system where moisture, carbon dioxide, and hydrocarbons are removed. The air then passes through heat exchangers where it is cooled to cryogenic temperature. The air then enters a high pressure distillation column where it is physically separated into a gaseous form of nitrogen at the top of the column and a liquid form of “crude” oxygen (~90%) at the bottom.

ASU生产过程从一个主气流压缩机开始，产品储存罐的输出后结束。空气通过一个去除了水蒸汽、二氧化碳和碳氢化合物的清洁系统压缩和输运。接着空气通过热交换器冷却到低温。随后空气进入高压分裂蒸馏塔，分离成气态氮和“原始”液氧（含大约90%的氧），氮蒸气在蒸馏塔顶部，液氧在蒸馏塔底部。

Argon is the major contaminant in this crude oxygen, which is then sent to a low-pressure distillation column where the oxygen is purified. The argon-rich waste stream from the low pressure column is sent to an argon distillation column. Some argon technologies distill the argon directly to its final manufacturing purity, while others utilize a separate step to purify it, for example, hydrogen deoxo. Purified argon is stored as a liquid in storage tanks at the site.

氩是原始氧中最大的杂质。接着把原始液氧送到低压分裂蒸馏塔净化。从低压塔流出的富氩废物被送到氩分裂蒸馏塔。某些氩技术直接把氩蒸馏到最终的生产纯度，而其它技术采用分离的步骤来净化它，例如氢脱氧。净化的氩以液态形式储存在现场的储存罐。

Uses用途

Argon serves as a shielding gas to protect metals from oxidation during welding. Inert gas welding is the preferred method of joining several ferrous and nonferrous alloys.

焊接中，氩作为保护气防止金属氧化。惰性气体焊接是连接几种含铁和不含铁的合金的首选方法。

The metals and semiconductor manufacturing industries employ argon as a purge or inerting gas in furnaces, or other processing steps. In some instances, liquid argon is introduced and then vaporized over the surface of volatile or reactive molten metals to significantly reduce oxidation and/or volatility using an inert “blanket” of gas.

金属和半导体工业在熔炉内把氩作为净化或惰性气体。在某些情况下，引入液态氩，它蒸发在挥发物或活泼的熔化金属表面，作为惰性的气体“毯子”大大地减低了氧化和/或挥发。

High-volume flow rates of argon are introduced via specialized lances or “tuyeres” in a variety of melting and refining processes. The argon typically acts as a “shroud” gas to provide protection to the tuyere. It also promotes removal of impurities and/or dissolved gases in several refining processes.

在许多熔化和精炼过程中，通过特殊的喷管或鼓风口引入大量高流速氩。氩主要作为覆盖气体对鼓风口提供保护。在几种精炼过程中它还促进了杂质清除和/或气体的离散。

Argon is also widely used in the lighting industry for filling bulbs and in combination with other rare gases for special color effects.

氩还在照明工业得到了广泛应用，填充灯泡，以及同其它稀有气体一起用于获得特殊的颜色效果。

Health Effects对健康的影响

Since argon is odorless, colorless, tasteless, and non-irritating, it has no warning properties. Humans possess no senses that can detect the presence of argon. Argon is non-toxic and inert. It can act as a simple asphyxiant by displacing the oxygen in air to levels below that required to support life. Inhalation of argon in excessive amounts can cause dizziness, nausea, vomiting, loss of consciousness, and death. Death may result from errors in judgment, confusion, or loss of consciousness, which prevents self rescue. At low oxygen concentrations, unconsciousness and death may occur in seconds and without warning. Personnel, including rescue workers, should not enter areas where the oxygen concentration is below19.5%, unless provided with a self-contained breathing apparatus (SCBA) or airline respirator.

由于无嗅、无色、无味、无刺激性，氩没有警告性特征。人类没有能够探测到氩的存在的官能。氩无毒且不活泼。通过取代空气中的氧，使之下降到维持生命所必须的水平以下，它可以成为简单的窒息物。过量吸入氩会导致眩晕、恶心、呕吐、失去知觉和死亡。死亡可能来源于错误的判断、精神混乱或者阻止了自救的失去知觉。在低氧浓度情况下，意识不清和死亡会在几秒钟内发生，而且没有警告。除非备有自己式呼吸器（SCBA）或空气管呼吸器，任何人，包括救援人员，都不能进入氧浓度低于19.5%的区域。

For more information on oxygen-deficient atmospheres consult Air Products’ Safetygram-17,“Dangers of Oxygen-Deficient Atmospheres.”

要得到关于缺氧大气的更多信息，请参考Air Products的安全程序-17，“缺氧大气的危险”。

Containers容器

Argon is shipped and stored in high-pressure cylinders, tubes, or tube trailers depending upon the quantity required by the user. Containers are designed and manufactured according to applicable codes and specifications for the pressure sand temperatures involved. The quantity of product a container can hold is determined by its water capacity and pressure rating.

根据用户要求的量，使用高压钢瓶、管道或管道拖车来运输和储存氩。钢瓶的设计和制造是按照相应的压力和温度所适用的法规和规范。容器的产品容量有它的水容积和额定压力来决定。

Cylinders钢瓶

Cylinders are manufactured according to DOT regulations, which specify the material of construction, method of manufacture, testing, and what products they are permitted to be filled with, as well as other details. A cylinder is a hollow tube with a closed concave base that permits it to stand upright. The opposite end is tapered to a small opening, threaded to accommodate the installation of a valve. A threaded neck ring is attached to the tapered end to allow a protective cylinder cap to be installed. Cylinders may be used individually or in groups. When used in groups, the cylinders should be piped together, for stationary storage or to form portable banks.

钢瓶的制造依照交通部的规定，该规定指定了建材、制造和测试方法、允许填充的产品以及其它细节。钢瓶是中空的管道，封闭的底部是凹入的，这样可以直立起来。另一端是锥形开口，车有螺纹，以便安装阀门。锥状顶端装有带螺纹的颈环，可以安装保护性的钢瓶帽。钢瓶可以单个或成群使用。成群使用时，钢瓶要用管道连接到一起作为固定储存库或形成移动储存库。

Tubes管道

Tubes are manufactured according to DOT regulations or to ASME codes depending on whether they are used for transportation or mounted permanently at a site. Tubes are generally mounted on a truck-trailer chassis or railcar bed or placed at stationary locations when large amounts of argon are needed. A tube is a pipe that is tapered on both ends. Each end is threaded to allow the installation of valves, connections, or relief devices.

根据管道是用于运输或者永久安装在某处，按照DOT的规定或者ASME的规定制造管道。管道一般是安装在拖车底盘或有轨车底座上，或者当需要大量氩时放置在固定位置。管道两端是锥形。每一端都车有螺纹，以安装阀门、接头或减压装置。

Valve Connections阀门接头

The Compressed Gas Association (CGA) recommends three different connections for argon depending on the pressure of the container.

根据容器的压力，压缩气体协会（CGA）推荐了三种不同的接头。

Table 1: Compressed Argon Physical and Chemical Properties

表1：压缩氩的物理和化学性质

Chemical Formula分子式  Ar

Molecular Weight分子量  39.95

Boiling Point沸点 @ 1 atm  –302.6°F (–185.9°C)

Freezing Point凝固点 @ 1 atm  –308.8°F (–189.4°C)

Critical Temperature临界温度  –188.4°F (–122.4°C)

Critical Pressure临界压力  705.8 psia (48.0 atm)

Density密度, Liquid液体, @ BP, 1 atm  87.40 lb/scf

Density密度, Gas气体 @ 68°F (20°C), 1 atm  0.1034 lb/scf

Specific Gravity比重, Gas气体 (air空气=1) @ 68°F (20°C), 1 atm  1.38

Specific Gravity比重, Liquid (water水=1) @ 68°F (20°C), 1 atm  1.40

Specific Volume比容 @ 68°F (20°C), 1 atm  9.68 scf/lb

Latent Heat of Vaporization汽化潜伏热  2804 Btu/lb mole

Expansion Ratio膨胀率, Liquid to Gas液体到气体, BP to 68°F (20°C)  1 to 840

Fig. 2 A typical tube container system for bulk argon一个用于大量氩的典型的管道容器系统.

In addition, a high-integrity connection also known as a Diameter Index Safety System(DISS) connection has been assigned to argon. Cylinders containing argon at pressures up to3000 psig use a CGA 580 connection; cylinders with pressures between 3001 and 5500 psig use the CGA 680 connection; and cylinders with pressures between 5501 and 7500 psig use a CGA 677 connection. The DISS connection assigned to argon is 718. For detailed drawings of these connections, consult CGA’s Pamphlet V-1.For general drawings consult the Air Products“ Specialty Gases and Equipment Catalog.”

另外，指定了一种被称为直径指数安全系统（DISS）的高完整性接头用于氩的使用。氩的压力在3000 psig以下的钢瓶使用CGA 580接头；压力在3001到5500 psig之间的钢瓶使用CGA 680接头；压力在5501到7500 psig之间的钢瓶使用CGA 677接头。指定给氩的DISS接头是DISS718。要得到这些接头的详细图纸可以参考CGA手册V-1。要得到草图可以参考Air Products的“特种气体和装置目录”。

Pressure-Relief Devices减压装置

Argon containers are equipped with pressure-relief devices to protect from over pressurization. Argon cylinders less than 65” long use a frangible disk device. Cylinders over 65” use a combination device consisting of a frangible disk backed by a fusible alloy. Combination devices require that both the temperature and pressure requirements be reached before the device will relieve. For more on pressure-relief devices, see Air Products’ Safetygram-15,“Cylinder Pressure-Relief Devices.”

氩容器装备有减压装置，以便在过压时保护容器。长度小于65英寸的氩钢瓶使用易碎盘装置。大于65英寸的钢瓶使用由后面是可熔合金的易碎盘组成的组合装置。组合装置要求在装置减压前温度和压力都达到要求。要了解关于减压装置的更多情况，可以参考Air Products的安全程序-15，“钢瓶减压装置”。

Container Stampings钢瓶的印记

Each cylinder or tube is identified by stampings in the metal of the shoulder. Fig. 3 shows these stampings and their meanings.

可以通过肩部金属上的印记来鉴别每一个钢瓶或管道。图3描述了一个印记的例子和它们的含义。

Shipment of Gaseous Argon气态氩的运输

All shipments of compressed argon must comply with the DOT Code of Federal Regulations, Title 49. This applies to motor freight, rail, air, and water shipments. For air shipments, all packages must also comply with International Air Transport Association/International Civil Air Organization (IATA/ICAO) Dangerous Goods Regulations. Water vessel shipments must also be prepared in accordance with International Maritime Organization (IMO) regulations. All packaging used to transport argon must be either “UN/DOT Specification” or “UN/DOT Authorized” and in proper condition for transport. DOT Code of Federal Regulations, Title 49, specifies the following labeling and identification requirements:

所有压缩氩的运输必须遵守DOT Code of Federal Regulations的49条。这对汽车货运、铁路、空运和水运都有效。对于空运，所有包装还要遵守国际空运协会/国际民航协会（IATA/ICAO）危险货物的规定。水运还要遵守国际海运组织（IMO）的规定。所有用于运输氧的包装必须或者是“UN/DOT规范”或者是“UN/DOT授权”，而且状态良好。DOT Code of Federal Regulations第49条还规定了下列的对标志和鉴别的要求：

DOT Hazard Class危险等级: 2.2

DOT Shipping Label运输标志: Nonflammable Gas不可燃气体

DOT Placard标签: Nonflammable Gas不可燃气体

Identification Number鉴别号: UN1006

DOT Shipping Name货物名称: Argon, Compressed氩，压缩的

Fig. 1 Typical cylinder shapes and sizes.图1 典型钢瓶的形状和尺寸

Safety Considerations对安全的考虑

The hazards associated with argon are asphyxiation and the high pressure of the gas in containers and systems.

同氩相联系的危险是窒息和在容器和系统里的高压。

If oxygen-deficient atmospheres are suspected or can occur, use oxygen monitoring equipment to test for oxygen-deficient atmospheres. Review the appropriate Material Safety Data Sheet (MSDS).

如果怀疑空气中缺氧或缺氧可能发生，使用氧检测设备来测试缺氧空气。可以回顾一下合适的材料安全数据表（MSDS）。

Buildings建筑物

Provide adequate ventilation in areas using argon. Provide monitoring for areas where oxygen displacement may occur. OSHA has established 19.5% oxygen concentration as the minimum for working without supplied air.

必须为正在使用氩的地方提供充分的通风。对氧迁移可能发生的地方进行监测。OSHA确定19.5%作为没有补充空气情况下工作时氧的最小浓度。

Remember, argon has no warning properties!

记住，氩没有警告性特征！

Storage储存

• Cylinders should be stored upright in a well-ventilated, dry, cool, and preferably fire-resistant, secure area, which is protected from the weather.

钢瓶应该直立储存在通风良好、干燥、凉爽、最好防火的安全的不受天气影响的地方。

• Storage temperatures should NEVER exceed125°F (52°C) and the area should be free of combustible materials. Storage should be away from heavily traveled areas and emergency exits.

储存室温度禁止超过125°F (52°C)，而且不能有可燃材料。储存地应远离人员经常出入的地方和紧急出口。

• Oxygen must be separated from flammables and combustibles by 20 feet or a half-hour fire wall.

氧必须同可燃物和易燃物间隔至少20英尺，或者间隔一道半小时的防火墙。

• Post “No Smoking” and “No Open Flames” signs. Copies of signs may be downloaded from Air Products’3 Product Stewardship web site at www.51qiti.com

张贴“禁止吸烟”和“禁止明火”的标记。这些标记的拷贝可以从Air Products的网站上下载，网址是www.51qiti.com。

• Avoid areas where salt or other corrosive materials are present. Valve protection caps and valve outlet seals should remain on cylinders not connected for use.

避免储存在有盐或其它腐蚀性材料的地方。不使用时，阀门保护帽和阀门排气口密封应保持在钢瓶上。

• Separate full from empty cylinders. Avoid excessive inventory or storage time and keep good inventory records.

把空钢瓶和满钢瓶隔离开。避免库存过多和储存时间过长，做好库存记录。

• Use a first-in first-out system.

采用先进先出库存管理系统。

Handling操作

• If you experience any difficulty operating the container valve or with the container connections, discontinue use and contact the supplier. Use the proper connections.

如果你在操作容器阀门或容器接头时遇到任何困难，马上停止使用，并同供应商取得联系。使用正确的接头。

•DO NOT USE ADAPTERS! 禁止使用转换接头！

• Do not remove or interchange connections. 禁止移动或交换接头

• Use piping and equipment designed to withstand pressures to be encountered.

使用设计得能够承受遇到的压力的管道和设备

• It is recommended that all vents be piped to the exterior of the building.

建议所有的通风孔要输送到建筑物外部。

• Use a suitable hand truck designed for cylinder movement. Do not drag, roll, or slide containers on their sides.

使用设计用于钢瓶搬运的合适的手推车。禁止拖拉、旋转或滑动容器。

• Never attempt to lift a cylinder by its cap. 禁止试图提着钢瓶帽举起钢瓶。

• Secure cylinders at all times while in use. 使用时要一直保持钢瓶固定。

• Use a pressure reducing regulator or separate control valve to safely discharge gas from cylinder. 使用减压调整器或单个的控制阀来安全地从钢瓶中排出气体。

• Use a check valve to prevent reverse flow into the cylinder.

采用止回阀，防止回流入钢瓶。

• Do not overheat cylinder to increase pressure or discharge rate.

禁止使钢瓶过热来增加压力或流速。

•NEVER insert an object (e.g., wrench, screwdriver, pry bar, etc.) into valve cap openings. Doing so may damage the valve causing it to leak.

禁止把物体（如扳手、螺丝起子、撬杆等）插入阀门帽地开口处。这样做可能损伤阀门，导致泄漏。

• Use a special cap wrench or adjustable strap-wrench to remove over tightened or rusted caps. 使用专门的阀门帽扳手或活动扳手来卸开过紧或生锈的帽子。

Refilling or shipping compressed gas cylinders without the consent of the owner is a violation of Federal Law.

未经所有者同意重新灌装或运输压缩气体钢瓶是侵犯联邦法律的行为。

Personal Protective Equipment (PPE) 个人防护装备(PPE)

Personnel must be thoroughly familiar with properties and safety considerations before being allowed to handle argon and/or its associated equipment. Safety glasses, safety shoes, and leather work gloves are recommended to handle cylinders. In emergency situations, wear a self-contained breathing apparatus (SCBA).

在被允许使用氧和它的附件之前，操作者必须对它们的性质和安全问题十分熟悉。当操作钢瓶时，推荐使用安全眼镜、安全鞋和皮制工作手套。紧急形势下，使用自给式呼吸器。

First Aid急救

Persons suffering from lack of oxygen should be moved to fresh air. If the victim is not breathing, administer artificial respiration. If breathing is difficult, administer oxygen. Obtain immediate medical attention.

必须把缺氧的人转移到有新鲜空气的地方。如果受害者停止了呼吸，进行人工呼吸。如果呼吸困难，输氧。立刻寻求医生的帮助。

Self-contained breathing apparatus (SCBA)may be required to prevent asphyxiation of rescue personnel.

可能要求备有自给式呼吸器（SCBA），以防止救援人员窒息。

Fighting Fires救火

Since argon is nonflammable, special fire-fighting equipment and instructions are not needed. However, upon exposure to intense heat or flame, a cylinder containing argon may vent rapidly and/or rupture violently. Most cylinders are designed to vent contents when exposed to elevated temperatures. Pressure in a cylinder or other container can build up due to heat and it may rupture if the pressure-relief device fails to function.

由于氩不可燃，不需要特殊的救火设备和指导。但是，暴露于剧热或火焰时，装氩的钢瓶会迅速排出内容物和/或猛烈地破裂。大多数钢瓶设计得可以在暴露于高温时排出内容物。如果减压装置失效的话，容器内的压力会由于热而积累，从而导致钢瓶破裂。

1. Cylinder Specification钢瓶规范

• DOT–Department of Transportation, which is the regulatory body that governs the use of cylinders.

DOT-交通部，管理钢瓶使用的管理部门

• Specification of the cylinder type of material of construction (e.g., 3AA).钢瓶建材类型的规定（如3AA）

• Service or working pressure in pounds per square inch (e.g., 2,265 psi)设施或工作压力，单位为磅每平方英寸（如2,265 psi）

2. Cylinder Serial Number钢瓶序列号

• The letters SG precede the serial numbers for Specialty Gas cylinders.对于特种气体钢瓶，字母SG标在序列号之前

3. Registered Owner Symbol登记的所有者符号

• Symbol used to indicate the original owner of the cylinders.符号用于指示钢瓶的最初所有者。

• APROINC is a Registered Owner Symbol for Air Products. APROINC是Air Products的登记的所有者符号。

4. Date of Manufacture生产日期

• This date (month-year) also indicates the original hydrostatic test.该日期（月-年）还说明了最初的流体静力学测试的日期。

5. Neck Ring Identification颈环鉴别

• The cylinder neck ring displays the name of the current owner of the cylinder.颈环显示着钢瓶现在的所有者的名字。

6. Retest Markings再测试记号

• The format for a retest marking is: Month–Facility–Year–Plus Rating–Star Stamp.再测试记号的格式是：月-设备-年-过量等级-星形标记

• The + symbol (Plus Rating) indicates that the cylinder qualifies for 10% overfill.加号（过量等级）说明钢瓶可以过量灌装10%

• The H symbol (Star Stamp) indicates that the cylinder meets the requirements for 10-year retest.符号H（星形标记）说明钢瓶满足10年后再测试的要求

7. CylinderTrak钢瓶的追踪

Bar Code Label条形码标记

• The Cylinder Trak bar code label provides a unique cylinder identifier and is used by computer systems

to track cylinders throughout the fill process. As an optional service, we have the capability of tracking cylinders to and from customers.

钢瓶的条形码标记为每个钢瓶提供了唯一的标志符号，计算机系统用它来在整个灌装过程中追踪钢瓶。作为一项可以选择的服务，我们有追踪来往于消费者的钢瓶的能力。

8. Cylinder Manufacturer’s Inspection Marking钢瓶制造商的检测标记

9. Cylinder Tare (Empty) Weight钢瓶皮（空）重

Fig. 3 Key to cylinder stampings. 图3 钢瓶印记的说明

Fig. 4 Nonflammable gas shipping label. .图4不可燃气体运输标志

Rescue in Oxygen-deficient Atmospheres缺氧空气里的救援

Fiction: I can hold my breath long enough to rescue a downed co-worker.

虚构：我能够屏住呼吸足够长的时间来营救倒下的工友。

Fact: Over 50% of the workers who die in confined spaces are attempting to rescue other workers.

事实：超过50%的死在狭窄空间的工人正在试图营救其他工人。

Never enter an oxygen-deficient atmosphere (<19.5% O2) without self-contained breathing apparatus.

禁止未戴自给式呼吸器进入缺氧空气（氧含量小于19.5%）。

Emergency Response System紧急反应系统

• Call呼叫: +1 (800) 523-9374 (Continental U.S. and Puerto Rico美国大陆和波多黎各)

• Call呼叫: +1 (610) 481-7711 (Other locations其它地方)

• 24 hours a day, 7 days a week一天24小时，一周七天

• For assistance involving Air Products and Chemicals, Inc. gases and equipment.

Technical Information Center技术资料中心

• Call呼叫: +1 (800) 752-1597 (U.S美国.)

• Call呼叫: +1 (610) 481-8565 (Other locations其它地方)

• Fax传真: +1 (610) 481-8690

• E-mail电子邮件: gasinfo@apci.com

• Monday星期一–Friday星期五, 8:00 a.m.–5:00 p.m. EST

Product Safety Information产品安全资料

• For MSDS and Safety grams需要材料安全数据表和安全程序:

www.51qiti.com  stewardship

• Fax-on-Demand应要求发传真:

Call呼叫: +1 (800) 245-2746

• Enter MSDS Index No. 1000 for a complete list of available safety literature.

进入材料安全数据表第1000号可以获得现有的安全文献的全部目录

• 24 hours a day, 7 days a week一天24小时，一周七天